# 2022 Two Rivers Community Drinking Water Report

When Congress passed the 1996 Safe Drinking Water Act amendments the Environmental Protection Agency (EPA) was given the mandate to require public water systems to provide each customer with a water quality report every 12 months.

This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water.

About the Two Rivers Resort Water System

The Two Rivers water system is owned and operated by the Spokane Tribe of Indians. This system provides a yearly average of 55,000 gallons per day. Peak (summer) production is 140,000 gallons per day. The system provides water to over 700 customers in the Two Rivers area. The system was first constructed by the Spokane Tribe of Indians in 1995. The operations staff includes three maintenance/operations personnel.

Our water sources are two wells located north of the Spokane and Columbia River confluence on the Spokane Indian Reservation. The system is at an altitude of approximately 1400 feet above MSL.  One 6- inch well was drilled to 170 feet, while the 1st 12-inch well was drilled to approximately 180 feet and the 2nd 12- inch well was drilled to 240 feet.  The wells produce approximately 20 million gallons a year. The system is supplied by one ground water well #3.  Well #1 is no longer is service for drinking water and is used only for irrigation. Well #2 is in standby and used for emergency services.

Need More Information?

If you have any questions about this report or concerning your water utility, please contact Nicklas Eldred (509) 626-4406 or, Brodie Ford or Lam Chan at Public Works (509) 458-6546. We want our valued customers to be informed about their water utility. If you want to learn more or to receive a personal copy of this report, please contact the Spokane Tribal Natural Resource Department

Additional water quality information may be obtained from:

Environmental Protection Agency – Safe Drinking Water Hotline – 1-800-426-4791 or their Web site www.epa.gov/safewater

American Water Works Association Web site www.awwa.org

About Drinking Water

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radio-active material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water before we treat it include:

• Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife.

• Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining or farming.

• Pesticides and herbicides, which may come from a variety of sources such as agriculture and residential uses.

• Radioactive contaminants, which are naturally occurring.

• Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can come from gas stations, urban storm water runoff, and septic systems.

It is because of these potential contaminants that we routinely evaluate our water source(s) to identify any potential sources of contamination. If you would like more information on our source protection plan call Nicklas Eldred 626-4406.

## Cross Connection Control Survey

The purpose of this survey is to determine whether a cross-connection may exist at your home or business. A cross connection is an unprotected or improper connection to a public water distribution system that may cause contamination or pollution to enter the system. We are responsible for enforcing cross-connection control regulations and ensuring that no contaminants can, under any flow conditions, enter the distribution system. If you have any of the devices listed below please contact us so that we can discuss the issue, and if needed, survey your connection and assist you in isolating it if that is necessary.

Underground lawn sprinkler system

Pool or hot tub

Decorative pond

Watering trough

Radiant heater

Water Quality

All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline at 1-800-426-4791.

As required by EPA, Two Rivers Water System routinely monitors for over 80 constituents in your drinking water. This table shows the results of our monitoring. All drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some constituents.  It's important to remember that the presence of these constituents does not necessarily pose a health risk.

Significant Deficiencies

A significant deficiency can include a flaw in design, operation, or maintenance, or a failure or malfunction of the sources, treatment, storage, or distribution system that EPA determines to be causing, or has the potential for introducing contamination into the water delivered to consumers.

Finished Water Storage

- It is unknown if water storage structure/tank #1 (ST-01) is clean and free from contamination since no documentation was provided of the tank having been inspected and/or cleaned since in went into service in 1994. Storage tanks should be inspected and/or cleaned, as necessary, every 5-10 years. Please send EPA documentation of water storage structure/tank #1’s last inspection or cleaning if completed within the past 10 years. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

- It is unknown if there is an overflow provided for storage structure/tank #1 that discharges to daylight in a way that will preclude the possibility of backflow to the reservoir and, where practical, provided with a metal screen or flapper valve. Please send photo documentation to EPA. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

- Lacking the proper keys, the surveyor was unable to climb storage structure/tank #1 (ST-01) to evaluate if air vents are properly protected and screened to prevent accidental contamination of the finished water, nor if access manhole openings were 4 inches or greater above the reservoir roof surface, with a lid 2 inches overlapping watertight and locked. Please send photo documentation for each of these items to the EPA. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

- It is unknown if overflow lines, air vents, drainage lines or clean out pipe is turned downward or covered, screened, and terminated a minimum of 2 times the diameter of the water outlet above the ground or water storage structure/tank #1 (ST-01) surface; please send photo documentation and/or storage structure/tank inspection report to EPA. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

Distribution

- The system is not protected from obvious cross connections. This was identified on 4/4/2016 and is scheduled to be repaired by 4/19/2022.

- Annual testing of installed backflow prevention devices is required. This was identified on 4/15/2021 and is scheduled to be repaired by 4/19/2022.

System Management/Operation

- The Water System does not have an operation and maintenance manual; send manual to the EPA upon completion. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

- The Water System does not have an emergency response plan; send plan to the EPA upon completion. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

- The Water System does not have a Cross-Connection Control Program; send program plan to the EPA upon completion. This was identified on 4/15/2021 and is scheduled to be resolved by 4/19/2022.

Explanation of the Water Quality Data Table

The table below shows the results of our water quality analysis. Every regulated contaminant that we detected in the water, even the minutest traces, is listed here. The table contains the name of each contaminant, the highest level allowed by the regulations (MCL), the ideal goals for public health (MCLG), the amount detected, and the usual sources of such contamination.

Definitions for the abbreviations used in the table are found below the table.

2021 Regulated Contaminants Detected

Lead and Copper

Definitions:

Action Level:  The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Action Level Goal (ALG):  The level of a contaminant in drinking water below which there is no known or expected risk to health.  ALGs allow for a margin of safety.

| Lead and Copper | Date Sampled | MCLG | Action Level (AL) | 90th Percentile | # Sites Over AL | Units | Violation | Likely Source of Contamination |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Copper | 2021 | 1.3 | 1.3 | 0.0461 | 0 | ppm | N | Erosion of natural deposits; Leaching from wood preservatives; Corrosion of household plumbing systems. |
| Lead | 2021 | 0 | 15 | 0.433 | 0 | ppb | N | Corrosion of household plumbing systems; Erosion of natural deposits. |

Regulated Contaminants

| Inorganic Contaminants | Collection Date | Highest Level Detected | Range of Levels Detected | MCLG | MCL | Units | Violation | Likely Source of Contamination |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Arsenic | 06/10/2019 | 5.2 | 5.2 - 5.2 | 0 | 10 | ppb | N | Erosion of natural deposits; Runoff from orchards; Runoff from glass and electronics production wastes. |
| Nitrate [measured as Nitrogen] | 2021 | 2 | 2.35 - 2.35 | 10 | 10 | ppm | N | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits. |
| Nitrite [measured as Nitrogen] | 06/10/2019 | 0.011 | 0.011 - 0.011 | 1 | 1 | ppm | N | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits. |

# Violations Table

| Ground Water Rule |  |  |  |
| --- | --- | --- | --- |
| The Ground Water Rule specifies the appropriate use of disinfection while addressing other components of ground water systems to ensure public health protection. |  |  |  |
| Violation Type | Violation Begin | Violation End | Violation Explanation |
| FAILURE ADDRESS DEFICIENCY (GWR) | 10/15/2016 | 2021 | We failed to properly respond to a significant deficiency in our water system. The system is not protected from obvious cross connections. |

In the tables above you found many terms and abbreviations you might not be familiar with. To help you better understand these terms we've provided the following definitions:

Maximum Contaminant Level - The “Maximum Allowed” (MCL) is the highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal - The “Goal”(MCLG) is the level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.

Milligrams per liter (mg/L) - one part per million corresponds to one minute in two years or a single penny in $10,000.

Picocuries per liter (pCi/L) - picocuries per liter is a measure of the radioactivity in water.

Non-Detectable (ND)–levels of constituent were below the equipment limitations.

About MCL’s

MCL’s are set at very stringent levels. To understand the possible health effects described for many regulated constituents, a person would have to drink 2 liters of water every day at the MCL level for a lifetime to have a one-in-a-million chance of having the described health effect.

Health Considerations

Lead: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. The Spokane Tribe is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to two minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at www.epa.gov/safewater/lead.  (from National Primary Drinking Water Regulations Part 141.154, in the section called “Required additional health information”)

Copper: Copper is an essential nutrient, but some people who drink water containing copper in excess of the action level over a relatively short amount of time could experience gastrointestinal distress. Some people who drink water containing copper in excess of the action level over many years could suffer liver or kidney damage. People with Wilson's disease should consult their personal doctor.

Arsenic: Some people who drink water containing arsenic in excess of the MCL over many years could experience skin damage or problems with their circulatory system, and may have an increased risk of getting cancer.

Nitrate: Infants below the age of six months who drink water containing nitrate in excess of the MCL could become seriously ill and, if untreated, may die. Symptoms include shortness of breath and blue-baby syndrome.

Total Coliform: Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other potentially-harmful (fecal coliform and E. coli), bacteria may be present. Coliforms, if found in more samples than allowed, is a warning of potential problems.

What does this mean?

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

The Future

In our continuing efforts to maintain a safe and dependable water supply it may be necessary to make improvements in your water system. The costs of these improvements may be reflected in the rate structure. Rate adjustments may be necessary in order to address these improvements.

Thank you for allowing us to continue providing your family with clean, quality water this year. In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. These improvements are sometimes reflected as rate structure adjustments. Thank you for your understanding.