2022 Wellpinit H.S. Community Drinking Water Report

When Congress passed the 1996 Safe Drinking Water Act amendments the Environmental Protection Agency (EPA) was given the mandate to require public water systems to provide each customer with a water quality report every 12 months. 
This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water.

About the Wellpinit High School Water System
The Wellpinit High School water system is owned and operated by the Wellpinit School District. This system serves approximately 473 people during the school year and about 25 people during the summer. The water system is served by two groundwater wells, Well #1 and Well #2. The steel tank holds 500,000 gallons that is pumped from Well #2 at 57 gpm.   Chris Scott is the facilities manager for the school and manages various staff to maintain and operate the water system.  The system is sampled and reported by Nicklas Eldred from Dept. of Natural Resources.  Water quality samples are processed through Anatek Laboratories. TestAmerica Inc., and T- Creek Laboratory based on the constituent being sampled.  
Need More Information?
If you have any questions about this report or concerning your water utility, please contact Nicklas Eldred at (509) 626-4406 or, Larry Flett (509) 258-4535. We want our valued customers to be informed about their water utility. If you want to learn more or to receive a personal copy of this report, please contact the Spokane Tribal Natural Resource Department
 Additional water quality information may be obtained from:
Environmental Protection Agency – Safe Drinking Water Hotline – 1-800-426-4791 or their Web site www.epa.gov/safewater
American Water Works Association Web site www.awwa.org
About Drinking Water
The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radio-active material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water before we treat it include: 
• Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife. 
• Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining or farming. 
• Pesticides and herbicides, which may come from a variety of sources such as agriculture and residential uses. 
• Radioactive contaminants, which are naturally occurring. 
• Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can come from gas stations, urban storm water runoff, and septic systems.
It is because of these potential contaminants that we routinely evaluate our water source(s) to identify any potential sources of contamination. If you would like more information on our source protection plan call Nicklas Eldred 626-4406.  
Water Quality 
All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline at 1-800-426-4791.
As required by EPA, Wellpinit Water System routinely monitors for over 80 constituents in your drinking water. This table shows the results of our monitoring. All drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some constituents.  It's important to remember that the presence of these constituents does not necessarily pose a health risk.
Significant Deficiencies
The only certified operator is Brian Crossley who supervises the water testing.   EPA has identified that someone in the Tribal Utilities staff obtain operator certification as well. This was identified on 04/05/2017 and was scheduled to be completed on 1/3/2018.     
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Explanation of the Water Quality Data Table
The table below shows the results of our water quality analysis. Every regulated contaminant that we detected in the water, even the minutest traces, is listed here. The table contains the name of each contaminant, the highest level allowed by the regulations (MCL), the ideal goals for public health (MCLG), the amount detected, and the usual sources of such contamination. 
Definitions for the abbreviations used in the table are found below the table.
Lead and Copper
Definitions:
Action Level:  The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.
Action Level Goal (ALG):  The level of a contaminant in drinking water below which there is no known or expected risk to health.  ALGs allow for a margin of safety.

	Lead and Copper
	Date Sampled
	MCLG
	Action Level (AL)
	90th Percentile
	# Sites Over AL
	Units
	Violation
	Likely Source of Contamination



	Copper
	08/31/2020
	1.3
	1.3
	0.2
	0
	ppm
	N
	Erosion of natural deposits; Leaching from wood
preservatives; Corrosion of household plumbing systems.



	Lead
	08/31/2020
	0
	15
	3.7
	0
	ppb
	N
	Corrosion of household plumbing systems; Erosion of natural deposits.



Regulated Contaminants
	Inorganic Contaminants
	Collection Date
	Highest Level Detected
	Range of Levels Detected
	MCLG
	MCL
	Units
	Violation
	Likely Source of Contamination

	Antimony
	09/19/2019
	0.422
	0.422 - 0.422
	6
	6
	ppb
	N
	Discharge from petroleum refineries; fire retardants; ceramics; electronics; solder; test addition.

	Arsenic
	09/19/2019
	1.9
	1.9 - 1.9
	0
	10
	ppb
	N
	Erosion of natural deposits; Runoff from orchards; Runoff from glass and electronics production wastes.

	Barium
	09/19/2019
	0.0124
	0.0124 - 0.0124
	2
	2
	ppm
	N
	Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural deposits.

	Fluoride
	09/19/2019
	0.00005
	0.00005 - 0.00005
	4
	4.0
	ppm
	N
	Erosion of natural deposits; Water additive which promotes strong teeth; Discharge from fertilizer and aluminum factories.

	Nitrate [measured as Nitrogen]
	2021
	0.14
	0.14 - 0.14
	10
	10
	ppm
	N
	Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits.

	Nitrite [measured as Nitrogen]
	09/19/2019
	0.000154
	0.000154 - 0.000154
	1
	1
	ppm
	N
	Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits.





In the table above you found many terms and abbreviations you might not be familiar with. To help you better understand these terms we've provided the following definitions:
	Unit Descriptions

	Term
	Definition

	ppm
	ppm: parts per million, or milligrams per liter (mg/L)

	ppb
	ppb: parts per billion, or micrograms per liter (µg/L)

	mrem
	millirems per year (a measure of radiation absorbed by the body)

	pCi/L
	Picocuries per Liter: a measure of the radioactivity in water

	NA
	NA: not applicable

	ND
	ND: Not detected

	NR
	NR: Monitoring not required, but recommended.



	Important Drinking Water Definitions

	Term
	Definition

	AVG
	Regulatory compliance with some MCLs are based on running annual average of monthly samples.

	MCLG
	MCLG: Maximum Contaminant Level Goal: The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

	MCL
	MCL: Maximum Contaminant Level: The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

	TT
	TT: Treatment Technique: A required process intended to reduce the level of a contaminant in drinking water.

	AL
	AL: Action Level: The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

	Variances and Exemptions
	Variances and Exemptions: State or EPA permission not to meet an MCL or a treatment technique under certain conditions.

	MRDLG
	MRDLG: Maximum residual disinfection level goal. The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

	MRDL
	MRDL: Maximum residual disinfectant level. The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

	MNR
	MNR: Monitored Not Regulated

	MPL
	MPL: State Assigned Maximum Permissible Level

	Level 1 Assessment
	A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.

	Level 2 Assessment:
	A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.


.
Health Considerations
Lead: If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. The Spokane Tribe is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to two minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at www.epa.gov/safewater/lead.  (from National Primary Drinking Water Regulations Part 141.154, in the section called “Required additional health information”)

Copper: Copper is an essential nutrient, but some people who drink water containing copper in excess of the action level over a relatively short amount of time could experience gastrointestinal distress. Some people who drink water containing copper in excess of the action level over many years could suffer liver or kidney damage. People with Wilson's Disease should consult their personal doctor.

Nitrate: Infants below the age of six months who drink water containing nitrate in excess of the MCL could become seriously ill and, if untreated, may die. Symptoms include shortness of breath and blue-baby syndrome. 

Total Coliform: Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially-harmful (fecal coliform and E. coli), bacteria may be present. Coliforms, if found in more samples than allowed, is a warning of potential problems.

Fluoride: Some people who drink water containing fluoride in excess of the MCL over many years could get bone disease, including pain and tenderness of the bones. Children may get mottled teeth.

Alpha emitters: Certain minerals are radioactive and may emit a form of radiation known as alpha radiation. Some people who drink water containing alpha emitters in excess of the MCL over many years may have an increased risk of getting cancer. 

Barium: Some people who drink water containing barium in excess of the MCL over many years could experience an increase in their blood pressure.
Special Health Concerns
Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).  
 
The Future

In our continuing efforts to maintain a safe and dependable water supply it may be necessary to make improvements in your water system. The costs of these improvements may be reflected in the rate structure. Rate adjustments may be necessary in order to address these improvements.
Thank you for allowing us to continue providing your family with clean, quality water this year. In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. These improvements are sometimes reflected as rate structure adjustments. Thank you for your understanding.
